# Solar Ground-Mount Racking — Mechanical/Structural Handoff

Project: Off-grid (or grid-interactive — see §0) solar PV, Greensboro Bend, VT This document: the mechanical/structural (racking + foundation) workstream, for integration with the in-progress electrical procurement/assembly workstream. Status: Design verified against published engineering; pending final local sign-off and BOM stockpile netting. Source design: Vandewetering, Hayibo & Pearce, Designs 2022, 6, 41 (open-source, CERN-OHL-S license). DOI 10.3390/designs6030041. Drawings/calcs: osf.io/yx8mq.

How to read this: Treat the structural numbers as a strong, defensible engineering estimate that confirms member sizing — NOT a stamped calculation. A Vermont engineer should review before pour (now a quick check, since the analysis is done). Items needing action by the electrical project or the owner are tagged [ACTION] and collected in §8.

## 0. Critical upstream dependency: islanded vs. grid-interactive

The racking work was developed while the system architecture decision was still open. That decision drives real structural and electrical specifics. The electrical project has almost certainly already committed to a path — this handoff should INHERIT that decision, not re-open it.

- Path A — Islanded / true off-grid (grid feeds a DC-bus charger and/or a break-before-make transfer switch only; never paralleled with inverter output). Stays under VT homeowner § 910 exemption; no VEC Rule 5.500 interconnection; non-UL-listed Grade-B panels are acceptable.

- Path B — Grid-interactive (hybrid inverter synchronizes/blends with grid, e.g. Victron PowerAssist). Triggers VEC interconnection (Rule 5.500 + likely CPG), UL 1741 / anti-islanding requirements, and would disqualify the non-UL-listed Grade-B panels specified here.

[ACTION — electrical project] Confirm which path is committed. If Path B, the panel selection (§1) and several integration points (§7) change.

Utility: Greensboro Bend is served by Vermont Electric Cooperative (VEC). Interconnection (if Path B): VEC Power Planning, powerplanning@vermontelectric.coop, Rule 5.500 application → interconnection approval letter → CPG on ePUC.

## 1. Panels (the mechanical design basis)

- Module: Waaree 575 W bifacial, N-type TOPCon, dual-glass. (Signature Solar "Grade B, 31-panel pallet" SKU.)

- Dimensions: ~2.3 m × 1.13 m (90.6" × 44.6"), ~35 mm frame.

- Weight: ~62–69 lb each (dual-glass bifacial; heavier than glass-backsheet).

- Load rating: 5400 Pa front / 2400 Pa rear — exceeds design load (§3), so panels are structurally sufficient.

- NOT UL listed, no manufacturer warranty. Acceptable for Path A; a problem for Path B. [ACTION] see §0.

- Pallet: 31 panels, ~2,100 lb gross, ~92" × 46" footprint. Full array ≈ 17.8 kW.

[ACTION — owner/electrical project] Pull exact mounting-hole spacing from the Waaree datasheet. Needed to finalize the module-attach block placement (§5) and the cut list.

## 2. Phasing

| Phase | Panels | Approx DC | Purpose |
| --- | --- | --- | --- |
| Phase 1 | 14 | ~8 kW | Prove build method, foundation/frost detail, tilt/snow-shed behavior through one VT winter before committing the rest. |
| Phase 2 | 17 (remainder of pallet) | ~9.8 kW | Complete the array using Phase 1 learnings. |

This handoff is scoped to Phase 1 (14 panels) for the BOM and cut list. Structural design is identical for Phase 2.

## 3. Verified structural design (Greensboro Bend)

### Design loads (Appendix A method of source paper)

- Tilt: ~55° (off-grid winter-priority; steep tilt also sheds snow and reduces structural snow load).

- Snow slope factor Cs = (60 − tilt)/45 = (60−55)/45 = 0.11 (vs London's 0.58 at 34°). Steep tilt cuts the slope factor ~80%.

- Net effect: even though Greensboro ground snow (~65 lb/ft² ≈ 3.1 kPa) >> London's, the steep tilt sheds so aggressively that the surface snow load lands near the NBCC 1.0 kPa minimum, governed to ~1.0–1.3 kPa for planning.

- Governing load combination: 1.25D + 1.5S (snow-down dominant; wind uplift does not combine). Factored design load ≈ 1.8–2.2 kPa — comparable to London's 1.80 kPa.

- Conclusion: Greensboro design demand ≈ London demand. The published London member set transfers, with ONE upsize (below).

### Member verification vs. Table A7 (factored, No.1/2 SPF)

| Member | London demand | Table A7 capacity | Verdict |
| --- | --- | --- | --- |
| Inside joist | M = 1.10 kNm (2×8) | Mr(2×8) = 1.17 | Tight (~6%) → UPSIZE to 2×10 (Mr = 1.90) |
| Beam (2×8) | M = 0.50, V = 1.90 kN | Mr 1.17 / Vr 3.99 | OK ample |
| Back post (6×6) | M = 0.90, C = 2.70 kN | Mr 2.49 / Cr 142.9 | OK large margin |
| Front post (4×4) | C = 2.70 kN | Cr 57.8 | OK large margin |
| Outside joist (2×6) | M = 0.55 kNm | Mr 0.67 | OK |

The single required change from the published design: inside joists 2×8 → 2×10, to absorb the slightly higher load AND the longer span of the larger Waaree panel (2.3 m vs the paper's 2.0 m).

### Greensboro adaptations (locked)

- Tilt ~55° → joists cut at 55° (not the paper's 34°).

- Inside joists → 2×10.

- Frost footing: 4 ft min, plan up to 5 ft. (VT NEK frost depth ≥ paper's 1.2 m Canadian spec.) ~3 bags concrete/hole.

- Concrete: 30 MPa minimum (freeze–thaw; paper is explicit — 20 MPa only for non-freezing climates).

- Hardware: stainless or hot-dipped galvanized ONLY. Plain zinc-plated is not permitted outdoors (per paper). Stainless + WEEB washers at panel interface (corrosion isolation + NEC bonding).

- Hand-treat all field cuts and drilled holes with 2% copper naphthenate — essential for 25-yr life; every miter and bolt hole exposes untreated wood.

- Buried posts: below-ground/UC4A rated. Upper members: ground-contact rated.

- Ground clearance: keep bottom panel edge well above max snow depth + slide-off pile (avoid the "buried lower edge" failure common in NE ground mounts).

### Foundation pivot trigger

If footing digging hits ledge/bedrock before depth (common in the NEK), pivot from concrete-footed posts to the ballasted design (Vandewetering/Jamil/Pearce 2024, Designs 8(1):17; same OSF group). [ACTION] Owner to confirm soil vs. ledge at post locations before Phase 1 dig.

## 4. Material choice rationale (for procurement)

- Lumber: pressure-treated SPF, micronized copper azole (MCA) treatment (brands: MicroPro/LifeWood, Wolmanized Outdoor, YellaWood, SmartSense). MCA is aluminum-safe (can contact panel frames) and less corrosive on fasteners — this is why MCA is specified over older ACQ.

- Why wood: ~49–77% cheaper than commercial metal racking (source paper); aluminum racking has >5× the embodied CO₂/kg of wood. Highly lumber-price-sensitive — see §6.

## 5. Phase 1 Bill of Materials (14 panels, landscape 2-high × 7-wide, ~8 post-pairs / 7 bays)

Three-column netting: the STOCKPILE column is intentionally blank. [ACTION — owner/electrical project] Walk the existing lumber pile and fill in usable quantities (by dimension, length, and treatment type — must be exterior/PT, ideally MCA; UNTREATED or interior lumber is NOT usable for structure). Then compute TO-PURCHASE = NEED − STOCKPILE.

| # | Member | Spec | NEED (qty) | STOCKPILE (fill in) | TO-PURCHASE |
| --- | --- | --- | --- | --- | --- |
| 1 | Back posts | 6×6, below-ground rated, ~3 m, MCA | 8 | _____ | _____ |
| 2 | Front posts | 4×4, below-ground rated, MCA | 8 | _____ | _____ |
| 3 | Beams | 2×8, MCA | ~16 | _____ | _____ |
| 4 | Inside joists | 2×10, MCA (cut 55°) | ~14 | _____ | _____ |
| 5 | Outside joists | 2×6, MCA (cut 55°) | 2 | _____ | _____ |
| 6 | Lateral bracing | 2×4, MCA | ~20 | _____ | _____ |
| 7 | Module-attach blocks | scrap/offcut MCA lumber | ~56 | _____ (likely from stockpile) | _____ |
| 8 | Footing concrete | 30 MPa min, ~3 bags/hole | ~48 bags (16 holes) | n/a | 48 bags |
| 9 | Beam-post bolts | ½" carriage (6" & 8"), SS or HDG, nut+washer | ~32 sets | n/a | ~32 |
| 10 | Module bolts | ¼" × 2½" stainless + WEEB washers | ~56 sets | n/a | ~56 |
| 11 | Fence brackets | joist/brace connections, HDG | ~60 | n/a | ~60 |
| 12 | Deck screws | 2½" exterior-rated | 2–3 lb | _____ | _____ |
| 13 | Joist hanger nails | 1½", HDG | 1–2 lb | n/a | as needed |
| 14 | Copper naphthenate | 2% solution (field cut treatment) | 1 qt | n/a | 1 qt |
| 15 | Clear stone | 150 mm at footing base (if bearing marginal) | as needed | _____ | _____ |

Quantities are planning figures. Final counts depend on confirmed bay layout and panel mounting-hole geometry (§1 action). Cut list (exact lengths + 55° angles) is the next deliverable once hole spacing is known.

## 6. Cost & labor (Phase 1)

- Materials estimate: ~$1,400–$2,800 USD for 14 panels (~8 kW), reflecting the 2×10 upsize, deeper frost footings, and stainless hardware. Stockpile lumber reduces this — net after filling §5.

- HIGHLY lumber-price-dependent. Source paper's caveat governs. Get a local VT quote for MCA-treated SPF before committing. (Paper's reference: US PT 2×4×8 ≈ $9.68 at time of writing; lumber has been volatile.)

- Labor: ~2 weekends, 3 builders. Dominant task = digging 16 frost-depth (4–5 ft) footings → rent a gas auger. Weekend 1: dig/set posts/pour. Cure. Weekend 2: beams/joists/blocks/panels/bonding. Panels are ~65 lb and 7.5 ft — 2 people per panel, carry vertically (dual-glass, both faces are glass).

## 7. Electrical ↔ structural integration points

These are where the racking design and the in-progress electrical workstream must agree. [ACTION — electrical project] reconcile each:

- Grounding / bonding: WEEB washers at each module-to-rack point provide the equipment bond. Confirm this satisfies the electrical project's NEC 690/250 bonding plan, or coordinate a separate bonding conductor. Wood rack is non-conductive — bonding strategy differs from a metal rack.

- Rapid shutdown (NEC 690.12, VT-amended): initiation device at a readily accessible location outside the building. NOTE: 2023 NEC adds an exception for arrays not attached to a building — this ground mount may qualify for relief. Electrical project to confirm whether RSD is required for the detached array and, if so, site the device.

- Conduit entry / trenching: DC (or AC) run from array to house. Trench to NEC depth (18" or 24" for RMC). Coordinate conduit stub-up location relative to the rack's rear posts and the array's electrical low end.

- Equipment mounting: combiner/disconnect/rapid-shutdown enclosures — decide if rack-mounted (on rear posts) or house-mounted. Affects post selection and bracing if rack-mounted.

- Wire management: clips/runs along joists and beams; keep off the ground, allow for thermal expansion and snow slide.

- Inverter/charger/battery location: per the earlier architecture work — if Path A islanded with a DC-bus charger or transfer switch, vs Path B hybrid inverter. Drives the array-to-equipment conductor sizing (NEC 690.8 / 710.15) the electrical project owns.

- NFPA 855 (2020, VT-adopted) signage (battery/ESS side, electrical project's scope): exterior signage on primary service entrance + location designator (G/B/L#) — VT amendment.

- Module electrical layout vs. mechanical layout: 14-panel string/series-parallel configuration (electrical) must be compatible with the 2-high × 7-wide physical layout (mechanical). Reconcile string boundaries with the bay/row geometry.

## 8. Open actions (consolidated)

| # | Action | Owner |
| --- | --- | --- |
| A1 | Confirm committed architecture: Path A islanded vs Path B grid-interactive (§0). If Path B, revisit panel UL-listing (§1). | Electrical project |
| A2 | Pull Waaree mounting-hole spacing from datasheet (§1) → enables cut list. | Owner / electrical project |
| A3 | Walk lumber stockpile; fill STOCKPILE column (§5) with exterior/PT lumber only. | Owner |
| A4 | Get local VT MCA-treated SPF lumber quote (§6). | Owner |
| A5 | Confirm soil vs. ledge at post locations; if ledge, pivot to ballasted foundation (§3). | Owner |
| A6 | Confirm Greensboro exact ground snow value + frost depth with VT Div. of Fire Safety AHJ / local code. | Owner |
| A7 | VT engineer review of completed analysis before pour (quick check, not from-scratch). | Owner |
| A8 | Reconcile all §7 electrical-integration points. | Electrical project |

## 9. Reference design — published specs (for traceability)

London, ON 34° reference rack (the validated base design this adapts):

- Back posts 6×6 (cut 2.7 m); front posts 4×4 (cut 1.6 m); beams 2×8; inside joists 2×8; outside joists 2×6; 2×4 bracing.

- Footings: 4 holes ≥250 mm dia, ≥1.2 m deep, 30 MPa concrete.

- 500 mm ground clearance; designed for 80 mph wind + snow.

- Build time 7.5 h / unit / 2 builders. Cost CAD $388.78 (~$0.32 CAD/W).

- Connections: ½" carriage bolts (beam-post), ¼" carriage bolts (module-block), fence brackets + joist-hanger nails, deck screws.

- License: CERN-OHL-S (free to use/modify/redistribute). Full drawings & calcs: osf.io/yx8mq.

Table A7 capacities (factored, No.1/2 SPF), for re-checks: | Lumber | Mr [kNm] | Vr [kN] | Tr [kN] | Cr [kN] | |---|---|---|---|---| | 2×4 | 0.27 | 1.93 | 9.65 | 24.66 | | 2×6 | 0.67 | 3.03 | 15.18 | 38.79 | | 2×8 | 1.17 | 3.99 | 19.95 | 50.98 | | 2×10 | 1.90 | 5.09 | 25.48 | 65.12 | | 2×12 | 2.82 | 6.20 | 31.01 | 79.25 | | 4×4 | 0.64 | 4.52 | 22.60 | 57.76 | | 6×6 | 2.49 | 11.18 | 55.92 | 142.92 |